## DC
title[alternative] | contributor[author] | date[issued] | publisher | identifier[bibliographicCitation] | abstract | abstract | keywords[*] | identifier[govdoc] | identifier[isbn] | identifier[issn] | identifier[ismn] | identifier[uri] | identifier[url] | identifier[doi(resolver)]
| Ahn, KH; Song, KG; | 2000-08-10 | ELSEVIER SCIENCE BV | DESALINATION, v.129, no.3, pp.207 - 216 | A study was conducted to investigate the treatability of a new microfiltration system utilizing agitator-induced flushing of the membrane to prevent fouling for wastewater reclamation. A hollow-fiber membrane was immersed in the tank and permeate was filtered through the membrane by intermittent suction using a pump. Influent from the large-scale resort complex was used. In the tank an agitator was operated at 350 rpm, with clockwise (4 s) - stop (1 s) - counter-clockwise (4 s) rotation cycle. Membrane pore size, permeate flux and suction mode were studied. The optimal operational setting was determined to be 0.02 m/h flux, with 10-min suction and 2-min idle permeate pumping cycle. This setting was capable of 77 days of continuous operation without chemical cleaning. Below 20 mg/L of COD, 3.5 mg/L of TOC, 0.2 NTU of turbidity and no suspended solids were contained in the effluent. This system was adequate for the reuse of wastewater for secondary applications such as in toilet flushing. |  | CROSS-FLOW MICROFILTRATION; WATER; FILTRATION; CROSS-FLOW MICROFILTRATION; WATER; FILTRATION; wastewater reuse; microfiltration (MF); membrane; intermittent suction; agitator-induced flushing; critical flux; suction mode; |  |  | 0011-9164 |  | https://pubs.kist.re.kr/handle/201004/141168