## DC
title[alternative] | contributor[author] | date[issued] | publisher | identifier[bibliographicCitation] | abstract | abstract | keywords[*] | identifier[govdoc] | identifier[isbn] | identifier[issn] | identifier[ismn] | identifier[uri] | identifier[url] | identifier[doi(resolver)]
| Ahn, HS; Yoon, ES; Sohn, DG; Kwon, OK; Shin, KS; Nam, CH; | 1996-02 | BUTTERWORTH-HEINEMANN LTD | TRIBOLOGY INTERNATIONAL, v.29, no.2, pp.161 - 168 | In order to identify the level of contamination of lubricating oil in a turbine-generator at a local power plant, contaminant analysis was conducted. The contaminant analysis was also used to assess the condition of tribe-components such as bearings, gears and bearing deflectors. Oil samples were taken and the debris in the used lubricating oil were analysed off-line to provide information for the construction of an on-line monitoring system. Statistical analysis of debris was also carried out to determine the quantitative trend of oil contamination. The on-line contaminant monitoring system was then developed with the capabilities to provide an early warning of excessive oil contamination and to detect any impending failures of tribe-components. Guidelines necessary for maintenance engineers such as preset warning level and a trip level (automatic shutdown) of contamination were established. In the system, a device utilizing a filter blockage principle was employed to measure the contamination level. The on-line system developed was installed and field tested in a turbine-generator at a local power plant. During the two year period of investigation, the lubricating system and related tribo-components were revealed to be in normal condition. |  |  |  |  | 0301-679X |  | https://pubs.kist.re.kr/handle/201004/144553